## GOOSE attacks
Attack condition | FDI Type | Label | Attack Targets | No. of datasets | Sub-scenario ID | Descriptions | Untrusted IEDs | Malicious Program ID | Time sections of successive behaviours in seconds
In fault-free operations, compromised IEDs mislead CBs with counterfeit opening signals to disrupt the power supply | Add | 811 | IED_XFMR1 | 1 | 8111a | (8111, 8121, 8131) Inject 40 messages with a 500ms HeartBeat (HB) to mislead CBs with counterfeit opening signals every 1 mins | IED_PIOC_XFMR1 | 8111 | Fault-free |  | Attacks | Fault-free |  | Attacks | Fault-free |  | Attacks | Total
|  |  | IED_XFMR2 | 1 | 8111b |  | IED_PIOC_XFMR2 | 8111 | 60 |  | 20 | 60 |  | 20 | 60 |  | 20 | 240
|  | 812 | IED_FDR (22kV) | 2 | 8121a-8121b |  | IED_PIOC_FDR | 8121a-8121b
|  | 813 | IED_FDR (FDR) | 4 | 8131a-8131d |  |  | 8131a-8131d
|  | 811 | IED_XFMR1 | 1 | 8112a | (8112, 8122, 8132) Inject 40 messages with a 250ms HB to mislead CBs with counterfeit opening signals every 1 mins | IED_PIOC_XFMR1 | 8112 | Fault-free |  | Attacks | Fault-free |  | Attacks | Fault-free |  | Attacks | Total
|  |  | IED_XFMR2 | 1 | 8112b |  | IED_PIOC_XFMR2 | 8112 | 60 |  | 10 | 60 |  | 10 | 60 |  | 10 | 210
|  | 812 | IED_FDR (22kV) | 2 | 8122a-8122b |  | IED_PIOC_FDR | 8122a-8122b
|  | 813 | IED_FDR (FDR) | 4 | 8132a-8132d |  |  | 8132a-8132d
|  | 811 | IED_XFMR1 | 1 | 8113a | (8113, 8123, 8133) Inject 15 messages with 1,4,16,64,256,1000ms HBs to mislead CBs with counterfeit opening signals every 1 mins | IED_PIOC_XFMR1 | 8113 | Fault-free |  | Attacks | Fault-free |  | Attacks | Fault-free |  | Attacks | Total
|  |  | IED_XFMR2 | 1 | 8113b |  | IED_PIOC_XFMR2 | 8113 | 60 |  | 10 | 60 |  | 10 | 60 |  | 10 | 210
|  | 812 | IED_FDR (22kV) | 2 | 8123a-8123b |  | IED_PIOC_FDR | 8123a-8123b
|  | 813 | IED_FDR (FDR) | 4 | 8133a-8133d |  |  | 8133a-8133d
|  | 811 | IED_XFMR1 | 1 | 8114a | (8114, 8124, 8134) Inject 10 messages with 1,4,16,64,256,1000ms HBs to mislead CBs with counterfeit opening signals every 1 mins | IED_PIOC_XFMR1 | 8114 | Fault-free |  | Attacks | Fault-free |  | Attacks | Fault-free |  | Attacks | Total
|  |  | IED_XFMR2 | 1 | 8114b |  | IED_PIOC_XFMR2 | 8114 | 60 |  | 5 | 60 |  | 5 | 60 |  | 5 | 195
|  | 812 | IED_FDR (22kV) | 2 | 8124a-8124b |  | IED_PIOC_FDR | 8124a-8124b
|  | 813 | IED_FDR (FDR) | 4 | 8134a-8134d |  |  | 8134a-8134d
| Alter | 821 | IED_XFMR1 | 1 | 8211a | (8211, 8221, 8231) Alter 10 messages to mislead CBs with counterfeit opening signals every 1 mins (st and HB unchange) | IED_PIOC_XFMR1 | 8211 | Fault-free |  | Attacks | Fault-free |  | Attacks | Fault-free |  | Attacks | Total
|  |  | IED_XFMR2 | 1 | 8211b |  | IED_PIOC_XFMR2 | 8211 | 60 |  | 10 | 60 |  | 10 | 60 |  | 10 | 210
|  | 822 | IED_FDR (22kV) | 2 | 8221a-8221b |  | IED_PIOC_FDR | 8221a-8221b
|  | 823 | IED_FDR (FDR) | 4 | 8231a-8231d |  |  | 8231a-8231d
|  | 821 | IED_XFMR1 | 1 | 8212a | (8212, 8222, 8232) Alter 10 messages to mislead CBs with counterfeit opening signals every 1 mins (st+1 and HB changes to 1,4,16,64,256,1000ms) | IED_PIOC_XFMR1 | 8212 | Fault-free |  | Attacks | Fault-free |  | Attacks | Fault-free |  | Attacks | Total
|  |  | IED_XFMR2 | 1 | 8212b |  | IED_PIOC_XFMR2 | 8212 | 60 |  | 5 | 60 |  | 5 | 60 |  | 5 | 195
|  | 822 | IED_FDR (22kV) | 2 | 8222a-8222b |  | IED_PIOC_FDR | 8222a-8222b
|  | 823 | IED_FDR (FDR) | 4 | 8232a-8232d |  |  | 8232a-8232d
[12 empty] | DMZ | The DMZ represents a buffer between the 1st attack cycle and the 2nd attack cycle. Two different colours of DMZ indicate two different statuses.
When short-circuit faults happen, compromised IEDs mislead associated CBs with counterfeit closing signals to disable safety protection | Add | 831 | IED_XFMR1 (66kV) | 1 | 8311a | (8311, 8321, 8331) Inject messages with a 500ms HB to mislead associated CBs with counterfeit closing signals | IED_PIOC_XFMR1 | 8311 | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total | DMZ | means outliers (non valid data) because MATLAB cannot process the physical behaviours of such attacks reasonably (transformers will be damaged physically in the real world). Data was labelled as N/V.
|  |  | IED_XFMR1 (XFMR) | 1 | 8311b |  |  |  | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8311c |  | IED_PIOC_XFMR2 | 8311 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8311d | [6 empty] | 30
|  | 832 | IED_FDR (22kV) | 2 | 8321a-8321b |  | IED_PIOC_FDR | 8321 |  |  |  | 30 |  |  |  |  | DMZ | means valid data that systems were recovered from a real/fabricated fault. Data was labelled as 0.
|  | 833 | IED_FDR (FDR) | 4 | 8331a-8331d |  |  | 8331 | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 831 | IED_XFMR1 (66kV) | 1 | 8312a | (8312, 8322, 8332) Inject 40 messages with a 500ms HB to mislead associated CBs with counterfeit closing signals | IED_PIOC_XFMR1 | 8312 | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8312b |  |  |  | 30 | 20 | 40 | 30 | 30 | 20 | 40 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8312c |  | IED_PIOC_XFMR2 | 8312 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8312d | [6 empty] | 30
|  | 832 | IED_FDR (22kV) | 2 | 8322a-8322b |  | IED_PIOC_FDR | 8322 |  |  |  | 30
|  | 833 | IED_FDR (FDR) | 4 | 8332a-8332d |  |  | 8332 | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 831 | IED_XFMR1 (66kV) | 1 | 8313a | (8313, 8323, 8333) Inject messages with 1,4,16,64,256,1000ms HBs to mislead associated CBs with counterfeit closing signals | IED_PIOC_XFMR1 | 8313 | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8313b |  |  |  | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8313c |  | IED_PIOC_XFMR2 | 8313 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8313d | [6 empty] | 30
|  | 832 | IED_FDR (22kV) | 2 | 8323a-8323b |  | IED_PIOC_FDR | 8323 |  |  |  | 30
|  | 833 | IED_FDR (FDR) | 4 | 8333a-8333d |  |  | 8333 | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 831 | IED_XFMR1 (66kV) | 1 | 8314a | (8314, 8324, 8334) Inject 30 messages with 1,4,16,64,256,1000ms HBs to mislead associated CBs with counterfeit closing signals | IED_PIOC_XFMR1 | 8314 | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8314b |  |  |  | 30 | 25 | 35 | 30 | 30 | 25 | 35 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8314c |  | IED_PIOC_XFMR2 | 8314 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8314d | [6 empty] | 30
|  | 832 | IED_FDR (22kV) | 2 | 8324a-8324b |  | IED_PIOC_FDR | 8324 |  |  |  | 30
|  | 833 | IED_FDR (FDR) | 4 | 8334a-8334d |  |  | 8334 | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
| Alter | 841 | IED_XFMR1 (66kV) | 1 | 8411a | (8411, 8421, 8431) Alter all messages to mislead associated CBs with counterfeit closing signals | IED_PIOC_XFMR1 | 8411 | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8411b |  |  |  | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8411c |  | IED_PIOC_XFMR2 | 8411 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8411d | [6 empty] | 30
|  | 842 | IED_FDR (22kV) | 2 | 8421a-8421b |  | IED_PIOC_FDR | 8421 |  |  |  | 30
|  | 843 | IED_FDR (FDR) | 4 | 8431a-8431d |  |  | 8431 | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 841 | IED_XFMR1 (66kV) | 1 | 8412a | (8412, 8422, 8432) Alter the first 30 messages to mislead associated CBs with counterfeit closing signals | IED_PIOC_XFMR1 | 8412 | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8412b |  |  |  | 30 | 25 | 35 | 30 | 30 | 25 | 35 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8412c |  | IED_PIOC_XFMR2 | 8412 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8412d | [6 empty] | 30
|  | 842 | IED_FDR (22kV) | 2 | 8422a-8422b |  | IED_PIOC_FDR | 8422 |  |  |  | 30
|  | 843 | IED_FDR (FDR) | 4 | 8432a-8432d |  |  | 8432 | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
When short-circuit faults happen, compromised IEDs mislead irrelevant CBs with counterfeit opening signals to trigger unnecessary protection, and thus, deteriorate the impacts of the short-circuit faults. | Add | 851 | IED_XFMR1 (66kV) | 1 | 8511a | (8511, 8521, 8531) Inject messages with a 500ms HB to mislead other irrelevant CBs with counterfeit opening signals until the associated CBs start to reset (the fault is eliminated and the systems recover). 66bus1-66bus2 (pair), XFMR1-XFMR2 (pair), 22bus1-22bus2 (pair), FDR1-FDR2 (pair), FDR3-FDR4 (pair) | IED_PIOC_XFMR1 | 8511 | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8511b |  |  |  | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8511c |  | IED_PIOC_XFMR2 | 8511 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8511d | [6 empty] | 30
|  | 852 | IED_FDR (22kV) | 2 | 8521a-8521b |  | IED_PIOC_FDR | 8521a-8521b |  |  |  | 30
|  | 853 | IED_FDR (FDR) | 4 | 8531a-8531d |  |  | 8531a-8531d | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 851 | IED_XFMR1 (66kV) | 1 | 8512a | (8512, 8522, 8532) Inject 40 messages with a 500ms HB to mislead other irrelevant CBs with counterfeit opening signals | IED_PIOC_XFMR1 | 8512 | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8512b |  |  |  | 30 | 20 | 40 | 30 | 30 | 20 | 40 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8512c |  | IED_PIOC_XFMR2 | 8512 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8512d | [6 empty] | 30
|  | 852 | IED_FDR (22kV) | 2 | 8522a-8522b |  | IED_PIOC_FDR | 8522a-8522b |  |  |  | 30
|  | 853 | IED_FDR (FDR) | 4 | 8532a-8532d |  |  | 8532a-8532d | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 851 | IED_XFMR1 (66kV) | 1 | 8513a | (8513, 8523, 8533) Inject messages with 1,4,16,64,256,1000ms HBs to mislead other irrelevant CBs with counterfeit opening signals until the associated CBs start to reset (the fault is eliminated and the systems recover). | IED_PIOC_XFMR1 | 8513 | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8513b |  |  |  | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8513c |  | IED_PIOC_XFMR2 | 8513 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8513d | [6 empty] | 30
|  | 852 | IED_FDR (22kV) | 2 | 8523a-8523b |  | IED_PIOC_FDR | 8523a-8523b |  |  |  | 30
|  | 853 | IED_FDR (FDR) | 4 | 8533a-8533d |  |  | 8533a-8533d | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 851 | IED_XFMR1 (66kV) | 1 | 8514a | (8514, 8524, 8534) Inject 30 messages with 1,4,16,64,256,1000ms HBs to mislead other irrelevant CBs with counterfeit opening signals | IED_PIOC_XFMR1 | 8514 | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8514b |  |  |  | 30 | 25 | 35 | 30 | 30 | 25 | 35 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8514c |  | IED_PIOC_XFMR2 | 8514 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8514d | [6 empty] | 30
|  | 852 | IED_FDR (22kV) | 2 | 8524a-8524b |  | IED_PIOC_FDR | 8524a-8524b |  |  |  | 30
|  | 853 | IED_FDR (FDR) | 4 | 8534a-8534d |  |  | 8534a-8534d | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
| Alter | 861 | IED_XFMR1 (66kV) | 1 | 8611a | (8611, 8621, 8631) when a short-circuit fault happens, an irrelevant IED (compromised with a malicious program) publishes packets containing tripping signals until the fault is eliminated and the systems recover. 66bus1-66bus2 (pair), XFMR1-XFMR2 (pair), 22bus1-22bus2 (pair), FDR1-FDR2 (pair), FDR3-FDR4 (pair) | IED_PIOC_XFMR1 | 8611 | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8611b |  |  |  | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8611c |  | IED_PIOC_XFMR2 | 8611 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8611d | [6 empty] | 30
|  | 862 | IED_FDR (22kV) | 2 | 8621a-8621b |  | IED_PIOC_FDR | 8621 |  |  |  | 30
|  | 863 | IED_FDR (FDR) | 4 | 8631a-8631d |  |  | 8631ab, 8631cd | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 861 | IED_XFMR1 (66kV) | 1 | 8612a | (8612, 8622, 8632) when a short-circuit fault happens, an irrelevant IED (compromised with a malicious program) publishes the first 30 packets containing tripping signals, and the rest packets containing non-tripping signals. | IED_PIOC_XFMR1 | 8612 | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8612b |  |  |  | 30 | 25 | 35 | 30 | 30 | 25 | 35 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8612c |  | IED_PIOC_XFMR2 | 8612 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8612d | [6 empty] | 30
|  | 862 | IED_FDR (22kV) | 2 | 8622a-8622b |  | IED_PIOC_FDR | 8622 |  |  |  | 30
|  | 863 | IED_FDR (FDR) | 4 | 8632a-8632d |  |  | 8632ab, 8632cd | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
Total Datasets (with labels) |  |  |  | 168 |  | Total malicious programs
When short-circuit faults happen, delete trip messages | Delete | 871 | IED_XFMR1 (66kV) | 1 | 871a | Delete the first 40 GOOSE trip packets when a fault occurs. Accordingly, delay protection for almost 35 seconds. | IED_PIOC_XFMR1 | 871 | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 871b |  |  |  | 30 | 35 | 55 | 30 | 30 | 35 | 25 | 240
|  |  | IED_XFMR2 (66kV) | 1 | 871c |  | IED_PIOC_XFMR2 | 871 |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 871d | [6 empty] | 30
|  | 872 | IED_FDR (22kV) | 2 | 872a-872b |  | IED_PIOC_FDR | 872 |  |  |  | 30
|  | 873 | IED_FDR (FDR) | 4 | 873a-873d |  |  | 873 | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
Additional Datasets (without labels) |  |  |  | 10 |  | Additional malicious programs

## Benign-behaviour-only
Scenario type | Label | No. of datasets | Descriptions | Time sections of successive behaviours in seconds |  |  |  | Total
Fault-free | 0 | 1 | No unusual events happen. | All fault-free |  |  |  | 270
|  |  |  | Fault-free | Emergency | Fault-free (recovery) | Emergency
Emergency operation | 101 | 1 | When a short-circuit fault occurs on Fault_66bus1, open CB1_66KV, CB2_66KV and CB_XFMR1; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 102 | 1 | When a short-circuit fault occurs on Fault_66bus2, open CB2_66KV, CB3_66KV and CB_XFMR2; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 103 | 1 | When a short-circuit fault occurs on Fault_XFMR1, open CB1_66KV, CB2_66KV and CB_XFMR1; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 104 | 1 | When a short-circuit fault occurs on Fault_XFMR2, open CB2_66KV, CB3_66KV and CB_XFMR2; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 105 | 1 | When a short-circuit fault occurs on Fault_22bus1, open CB1_22KV | 30 | 90 | 60 | 90 | 270
| 106 | 1 | When a short-circuit fault occurs on Fault_22bus2, open CB3_22KV | 30 | 90 | 60 | 90 | 270
| 107 | 1 | When a short-circuit fault occurs on Fault_FDR1, open CB_FDR1 | 30 | 90 | 60 | 90 | 270
| 108 | 1 | When a short-circuit fault occurs on Fault_FDR2, open CB_FDR2 | 30 | 90 | 60 | 90 | 270
| 109 | 1 | When a short-circuit fault occurs on Fault_FDR3, open CB_FDR3 | 30 | 90 | 60 | 90 | 270
| 110 | 1 | When a short-circuit fault occurs on Fault_FDR4, open CB_FDR4 | 30 | 90 | 60 | 90 | 270